## Sheet1
삭제 Del | 작업활동 및 내용 Work & Contents | 유해위험요인 및 환경측면 영향 Hazard & Risk | EHS | 피해형태 및 환경영향 Damage & Effect | 위험성 Risk Rate | 위험성 Risk Rate | 위험성 Risk Rate | 등급 Rate | 개선대책 및 세부관리방안 Corrective Action | 개선담당자 Responsibility | 개선일자 Action Date | 위험성 Risk Rate | 위험성 Risk Rate | 위험성 Risk Rate | 등급 Rate
삭제 Del | 작업활동 및 내용 Work & Contents | 유해위험요인 및 환경측면 영향 Hazard & Risk | EHS | 피해형태 및 환경영향 Damage & Effect | 빈도 Risk Rate | 강도 Severity | T | 등급 Rate | 개선대책 및 세부관리방안 Corrective Action | 개선담당자 Responsibility | 개선일자 Action Date | 빈도 Likelihood | 강도 Severity | T | 등급 Rate
false | Temporary Electricity | Electrocution / electric shock due to absence of grounding for distribution board | E | Physical | 2 | 3 | 6 | C | 1) Install copper grounding rod and connect body grounding of distribution board properly 2) Check resistance of copper grounding and must be below 5 ohms | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Temporary Electricity | Electric shock when worker connect the socket to the outlet of distribution board | E | Physical | 2 | 5 | 10 | B | 1) Install fence, lock system and only Authorized personnel only 2) Regularly check the condition of the socket outlets 3) regularly check the working condition of the ELCB / GFCI 4) Install dead front type covers to hide wiring connections | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Temporary Electricity | Electric shock caused by inadequate insulation and absence of ELCB | E | Physical | 3 | 5 | 15 | B | 1) Inspect if cable is 3-phase or double insulated 2) Check power source if provided with 30mA ELCB 3) Inspect if electrical DB is properly grounded | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Temporary Electricity | Electrocution / electric shock caused while conducting welding activity | E | Physical | 3 | 4 | 12 | B | 1) Insulate cable terminals with insulation tapes or covers 2) Set automatic shock protector and wear proper PPE | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Temporary Electricity | Slip / fall of worker on the same level due to poor cable management | E | Physical | 3 | 3 | 9 | C | 1) Arrange all electrical and welding cable in the work area 2) Coil and hang cables overhead using insulated post / S-bar | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Temporary Civil | Collapse of slope caused by unstable ground and change of ground-water level | E | Physical / Property | 2 | 4 | 8 | C | 1) Follow proper sloping depending on soil classification 2) Provide dewatering equipment to remove accumulated water and prevent scouring of excavation base 3) Install safety net for the excavation side slope | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Temporary Civil | Fire / explosion when hitting underground utilities during excavation | E | Physical / Property | 3 | 2 | 6 | C | 1) Check the location of underground utility before starting work 2) Relocate electric line, communication and gas line | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Temporary Civil | Personnel fall to excavation due to absence of fall prevention facility | E | Physical | 2 | 3 | 6 | C | 1) Install appropriate barricade along the perimeter of the excavation 2) Post warning / safety signage prominently | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Temporary Civil | Tumbling / falling due absence of proper access to excavation | E | Physical | 2 | 3 | 6 | C | 1) Provide proper and safe temporary access leading to excavated area 2) Provide handrails along the side of the temporary access | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Temporary Civil | Vehicle / equipment fall to excavation due to inadequate fall prevention facility / traffic & warning signage | E | Physical / Property | 2 | 3 | 6 | C | 1) Install earth dike / berm along the excavation edge 2) Provide safety / warning signage and traffic blinkers | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Temporary Fence | Overturning / fall of temporary fence due to strong wind during installation | E | Physical / Property | 1 | 2 | 2 | E | 1) Provide enough support during installation of temporary fence 2) Strictly supervise activity and suspend in case of strong wind condition | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Temporary Fence | Fall while using straight ladder when installing the temporary fence | E | Physical | 1 | 3 | 3 | D | 1) Use step / A-type ladder instead of straight ladder 2) Assign worker to support and hold the step ladder in place 3) Provide outrigger support for A-type ladder | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Temporary Fence | Cut / laceration while handling / installing the temporary fence | E | Physical | 2 | 2 | 4 | D | 1) Use proper hand gloves 2) Assign enough number of workers to install the temporary fence | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Temporary Fence | Back / hand pain due to repititive movement / manual handling of materials | E | Physical | 3 | 3 | 9 | C | 1) Lift materials less than 25 kilos 2) Provide frequent rest breaks to break monotony of movement | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Overturning of crane after setting too close to excavation edge | E | Physical / property | 2 | 4 | 8 | C | 1) Inspect the equipment & its documents and provide operation permit if permitted to work 2) Inspect the ground condition, provide steel plate on unstable or backfilled area 3) Assign 3rd party certified & competent crane operator | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Overturning of crane during lifting after bypassing the load capacity or boom radius | E | Physical / Property | 3 | 4 | 12 | B | 1) Inspect the equipment & its documents and provide operation permit if permitted to work 2) Check crane safety device including overload limiter and limit switch 3) Prepare lifting plan for critical lifting activity 4) Assign 3rd party certified & competent crane operator | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Material fall when round sling was cut after being in contact with the sharp edge of material being lifted | E | Physical / Property | 2 | 4 | 8 | C | 1)Check the lifting gears to be used before any lifting activity 2) Provide softener or pipe sleeve in areas where round sling is in contact with the sharp edge of the load 3) Lift using the lifting lugs provided 4) Barricade the lifting area and prohibit entry during lifting activity | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Material fall during lifting after using damaged lifting tackles (shackles) | E | Physical / Property | 3 | 4 | 12 | B | 1) Inspect all lifting tackles (shackles) to be used before the lifting activity start, inspection certificate 2) Prohibit anybody from entering the lifting area 3) Conduct high risk work last minute risk assessment 4) Assign 3rd party certified & competent rigger level 1 | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Material fall due to poor coordination between rigger and crane operator | E | Physical / Property | 3 | 4 | 12 | B | 1) Inspect the equipment & its documents and provide peration permit if permitted to work 2) Prepare lifting plan for critical lifting activity 3) Assign 3rd party certified & competent crane operator and rigger 4) Assign ONLY 1 rigger that will give signal to the crane operator 5) Conduct TBT prior to start of activity to discuss hazard of the job | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Material fall when lifting gears is detached from the hook block due to absence of safety latch | E | Physical / Property | 1 | 4 | 4 | D | 1) Check equipment using the daily equipment checklist before use 2) Check the safety latch of the main hook block to be in good working condition 3) High-risk work safety pre-qualification inspection 4) Barricade and strictly control personnel from entering the area | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Material fall due to loosened crane wire rope caused by improper revving | E | Physical / Property | 1 | 4 | 4 | D | 1) Inspect the equipment & its documents and provide operation permit if permitted to work 2) Check and inspect the equipment daily using the equipment checklist before use 3) Check crane safety device (limit switch, overload limit switch, crane monitor, etc) 4) Assign 3rd party certified & competent crane operator | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Material fall or personnel strike by load due to uncontrolled lowering of load | E | Physical / Property | 1 | 4 | 4 | D | 1) Inspect the equipment & its documents and provide operation permit if permitted to work 2) Inspect the equipment daily using the equipment checklist before use 3) Check crane safety device (limit switch, overload limit switch, crane monitor, etc) 4) Assign 3rd party certified & competent crane operator | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Material fall or personnel strike by load when lifting during strong wind | E | Physical / Property | 3 | 4 | 12 | B | 1) Strictly monitor the weather condition (wind condition), suspend lifting during strong winds 2) Follow lifting restriction depending on wind speed | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Personnel strike or hit by material during lifting due to absence of flagman | E | Physical / Property | 1 | 4 | 4 | D | 1) Assign trained flagman and provide megaphone to be used during high risk lifting activity 2) Restrict entry of personnel inside lifting area 3) Provide barricade & signage along the perimeter of lifting area | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Personnel hit or strike by load due to uncontrolled lifting / absence of tagline or guide rope | E | Physical / Property | 3 | 4 | 12 | B | 1) Assign competent worker to assist in lifting activity, holding the tag line or guide rope 2) Use minimum of 2-16mm diameter pp rope at least 20 meters in length or more as guide rope 3) Use megaphone or whistle to control people in the vicinity during the lifting activity | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Bending of crane boom while lifting heavy materials due to failure or not providing overload limit switch | E | Property | 3 | 4 | 12 | B | 1) Inspect the equipment & its documents and provide operation permit if permitted to work 2) Check and inspect the equipment daily using the equipment checklist before use 3) Check crane safety device (limit switch, overload limit switch, crane monitor, etc) 4) Assign 3rd party certified & competent crane operator | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Absence of barricade along the crane working radius injuring other personnel when the material accidentally falls | E | Physical / Property | 2 | 5 | 10 | B | 1) Provide barricade & signage along the perimeter of the crane working radius 2) Assign trained flagman 3) Strictly supervise lifting activity 4) Conduct LMRA before starting any high risk lifting activity | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting and Installation of Transformer | Personnel fall while removing the lifting gears from the lifting lug due to absence of proper access / working platform | E | Physical | 3 | 4 | 12 | B | 1) Provide appropriate length of step / straight ladder to be sued when removing the shackles from the lifting lug 2) Worker to wear and use full body harness 3) Assign helpers to hold the ladder in place 4) Follow safe guidelines for ladder use | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Shifting of panel using forklift | Material fall caused by improper / unsafe handling of material while using forklift | E | Physical / Property | 3 | 4 | 12 | B | 1) Check safe lifting requirement for materials based on its weight 2) Check safety condition of equipment before use | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Shifting of panel using forklift | Overturning of forklift due to bad ground condition | E | Physical / Property | 3 | 3 | 9 | C | 1) Flat and smooth ground 2) Potholes, uneven surface immediately covered | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Shifting of panel using forklift | Overturning / tumbling of load due to sudden stopping of forklift | E | Physical / Property | 3 | 4 | 12 | B | 1) Inspect the equipment & its documents and provide operation permit if permitted to work 2) Check forklift safety condition before starting work 3) Assign 3rd party certified & competent forklift operator | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Shifting of panel using forklift | Overturning of load due to unbalanced loading on the forklift forks | E | Physical / Property | 3 | 4 | 12 | B | 1) Inspect the equipment & its documents and provide operation permit if permitted to work 2) Check forklift safety condition before starting work 3) Check weight of material to be carried before using the equipment 4) Assign 3rd party certified & competent forklift operator | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Shifting of panel using forklift | Forklift hitting existing structure due to absence of flagman | E | Property | 3 | 3 | 9 | C | 1) Assign trained flagman when to assis forklift when shifting materials at site 2) Conduct TBT prior to start of activity | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Shifting of panel using forklift | Forklift hitting flagman due to operators vision obstructed by load | E | Property | 3 | 4 | 12 | B | 1) Assign trained flagman when to assis forklift when shifting materials at site 2) Conduct TBT prior to start of activity 3) Flagman to keep away at least 5 meters from the equipment | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Overturning of crane after setting too close to excavation edge | E | Physical / property | 2 | 4 | 8 | C | 1) Inspect the equipment & its documents and provide operation permit if permitted to work 2) Inspect the ground condition, provide steel plate on unstable or backfilled area 3) Check the ground settlement of outrigger support during setting-up of mobile crane 4) Set outriggers at least 2 meters from the edge of excavation area 5) Assign 3rd party certified & competent crane operator | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Overturning of mobile crane due to ground settlement of out-rigger's support during lifting | E | Physical / Property | 2 | 4 | 8 | C | 1) Inspect the ground condition, provide steel plate on unstable or backfilled area 2) Check the ground settlement of outrigger support during setting-up of mobile crane 3) Barricade the lifting area and prohibit entry of unwanted personnel | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Overturning / tumbling of mobile crane due to collapse of outrigger after failing to install the outrigger locking pins | E | Physical / Property | 2 | 4 | 8 | C | 1) Inspect the ground condition, provide steel plate on unstable or backfilled area 2) Check and ensure outrigger locking pins are placed | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Overturning / tumbling of mobile crane due to failure to fully extend the crane outriggers | E | Physical / Property | 2 | 4 | 8 | C | 1) Inspect the equipment daily using the equipment checklist 2) Check outriggers are fully extended and locking pins are engaged | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Overturning / tumbling of mobile crane due to equipment tyres not elevated and outrigger not properly set | E | Physical / Property | 2 | 4 | 8 | C | 1) Check & inspect set-up of crane before start of lifting activity, tyres of mobile crane elevated at least 1 inch from the ground | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Overturning of crane during lifting after bypassing the load capacity or boom radius | E | Physical / Property | 3 | 4 | 12 | B | 1) Inspect the equipment & its documents and provide operation permit if permitted to work 2) Check crane safety device including overload limiter and limit switch 3) Assign 3rd party certified & competent crane operator | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Material fall when web sling was cut after being in contact with the sharp edge of material being lifted | E | Physical / Property | 2 | 4 | 8 | C | 1)Check the lifting gears to be used before any lifting activity 2) Provide softener or pipe sleeve in areas where web sling is in contact with the sharp edge of the load 3) Lift using the lifting lugs provided 4) Barricade the lifting area and prohibit entry during lifting activity | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Material fall during lifting after using damaged lifting tackles (shackles) | E | Physical / Property | 3 | 4 | 12 | B | 1) Inspect all lifting tackles (shackles) to be used before the lifting activity start, inspection certificate 2) Prohibit anybody from entering the lifting area 3) Assign 3rd party certified & competent rigger | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Material fall due to breaking of web sling during lifting | E | Physical / Property | 3 | 4 | 12 | B | 1) Inspect all web slings to be used before the lifting activity start 2) Check SWL of lifting gears compared to the material to be lifted 3) Assign 3rd party certified & competent rigger | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Material fall when lifting gears is detached from the hook block due to absence of safety latch | E | Physical / Property | 1 | 4 | 4 | D | 1) Check equipment using the daily equipment checklist before use 2) Check the safety latch of the main hook block to be in good working condition 3) Barricade and control personnel from entering the lifting area | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Material fall due to loosened crane wire rope caused by improper / loosened revving | E | Physical / Property | 1 | 4 | 4 | D | 1) Inspect the equipment & its documents and provide operation permit if permitted to work 2) Check and inspect the equipment daily using the equipment checklist before use 3) Check crane safety device (limit switch, overload limit switch, crane monitor, etc) 4) Assign 3rd party certified & competent crane operator | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Material fall or personnel strike by load when lifting during strong wind | E | Physical / Property | 3 | 4 | 12 | B | 1) Strictly monitor the weather condition (wind condition), suspend lifting during strong winds 2) Follow lifting restriction depending on wind speed | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Personnel strike or hit by material during lifting due to absence of flagman | E | Physical / Property | 1 | 4 | 4 | D | 1) Assign trained flagman and provide megaphone to be used lifting activity 2) Restrict entry of personnel inside the lifting area by providing barricade & signage along the perimeter of the lifting area | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Personnel hit or strike by load due to uncontrolled lifting / absence of tagline or guide rope | E | Physical / Property | 3 | 4 | 12 | B | 1) Assign workers to assist in holding the tag line or guide rope 2) Use minimum of 2-16mm diameter pp rope at least 10 meters in length or more as guide rope 3) Use megaphone or whistle to control people in the vicinity during lifting activity | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Lifting & Shifting of Electrical Panel | Absence of barricade along the crane working radius injuring other personnel when the material accidentally falls | E | Physical / Property | 2 | 5 | 10 | B | 1) Provide barricade & signage along the perimeter of the crane working radius 2) Assign trained flagman and strictly supervise lifting activity | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false |  | Head injury from head bump and not wearing safety helmet | E | Physical | 3 | 5 | 15 | B | 1) Wear safety helmet with chin strap properly 2) Post head bump signage and protective cushion | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Cable termination, dressing and tagging | Fall on the same level due to poor management of cables / poor housekeeping | E | Physical | 2 | 5 | 10 | B | 1) Conduct regular housekeeping and remove waste / unwanted materials immediately 2) Arrange electrical cable by hanging overhead using insulated S-bar or cable posts | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Cable termination, dressing and tagging | Fingers and hand injury due to absence of appropriate safety gloves after getting in contact with pointed edge of cable wire | E | Physical | 3 | 3 | 9 | C | 1) Wear appropriate safety hand gloves for the activity 2) Exercise caution and conduct TBt to discuss hazard related to activity | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Cable termination, dressing and tagging | Fingers and hand injury due to carelessness when using crimping tools | E | Physical | 2 | 2 | 4 | D | 1) Wear appropriate safety hand gloves for the activity 2) Exercise caution and conduct TBt to discuss hazard related to activity | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Cable termination, dressing and tagging | Fingers and hand injury caused by using damage / defective hand tools | E | Physical | 3 | 3 | 9 | C | 1) Check and inspect condition of hand tools before use 2) Wear appropriate PPE in relation to the activity | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Cable termination, dressing and tagging | Finger / hand injury caused when using sharp blades during cable dressing | E | Physical | 3 | 3 | 9 | C | 1) Wear appropriate safety hand gloves for the activity 2) Exercise caution and conduct TBt to discuss hazard related to activity | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Cable termination, dressing and tagging | Material damage after cable is repeatedly trampled | E | Property | 2 | 2 | 4 | D | 1) Secure cable to be terminate and provide cover if necessary 2) Provide barricade around the cable to be terminated | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Cable termination, dressing and tagging | Health injury caused by no wearing appropriate mask and regularly inhaling fiber optic shards | E | Health | 3 | 4 | 12 | B | 1) Conduct TBT to discuss hazard related to the activity 2) Exercise caution and assign enough personnel for the activity 3) Provide appropriate PPE, hand gloves / face mask, aside from the other minimum required PPE | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Cable termination, dressing and tagging | Fire / explosion when using defective gas torch used for heat shrinking of insulator / tubing | E | Physical / Property | 3 | 3 | 9 | C | 1) Check / inspect blow torch to be used for signs of defect 2) Use butane powered torch and put off fire when not in use 3) Assign fire watchman equipped with fire extinguisher | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Cable termination, dressing and tagging | Fire / burn due to improper use of gas torch | E | Physical | 2 | 4 | 8 | C | 1) Check / inspect blow torch to be used for signs of defect 2) Use butane powered torch and put off fire when not in use 3) Assign fire watchman equipped with fire extinguisher | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Cable termination, dressing and tagging | Heat stress / exhaustion caused by working under the sun | E | Physical / Health | 3 | 4 | 12 | B | 1) Provide temporary rest shelter near the work area 2) Ensure supply of cool drinking water and ventilation fan to workers 3) Provide frequent breaks and avoid working between 12:00 ~ 15:00 Hrs. during the summer season | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E
false | Cable termination, dressing and tagging | Back / hand pain due to repititive movement | E | Physical | 3 | 3 | 9 | C | 1) Lift materials less than 25 kilos 2) provide regular rest breaks to disrupt monotony of movement 3) Assign enough personnel for the activity | sungil Heo | 2024-01-31 | 1 | 1 | 1 | E

## 코드목록 (hidden)
구분 | 코드
EHS | E
EHS | H
EHS | S
빈도 Risk Rate | 1
빈도 Risk Rate | 2
빈도 Risk Rate | 3
빈도 Risk Rate | 4
빈도 Risk Rate | 5
강도 Severity | 1
강도 Severity | 2
강도 Severity | 3
강도 Severity | 4
강도 Severity | 5
빈도 Likelihood | 1
빈도 Likelihood | 2
빈도 Likelihood | 3
빈도 Likelihood | 4
빈도 Likelihood | 5
강도 Severity | 1
강도 Severity | 2
강도 Severity | 3
강도 Severity | 4
강도 Severity | 5